ReVx EMS

Battery Energy Storage System

Software & Hardware Architecture

Product Specification & Implementation Guide

Scalable Platform: Residential (50 kWh) to Container (6+ MWh) & Beyond

Hardware: Advantech ECU-1170-552A  |  BMS: CAN DBC  |  PCS: Modbus RTU V1.24

BTMS + Meter + DG + PV  |  Cells: 16S–108S  |  Modules: 3–20/Rack  |  Multi-Source Priority

Version 3.2  |  February 2026  |  ReVx Energy  |  CONFIDENTIAL

# Table of Contents

1. Product Overview

1.1 Platform

1.2 Battery Hierarchy

1.3 Scaling Range

1.4 Design Principles

2. Architecture Diagrams

2.1 Battery

2.2 Software

2.3 Hardware

3. EMS State Machine & Interlock Logic

3.1 System States

3.2 State Transitions

3.3 Interlock Matrix

3.4 PCS Start Permissive Logic

4. Power Source Priority Logic

4.1 DAY Mode

4.2 NIGHT Mode

4.3 Source Manager

5. I/O Subsystems & Signal List

5.1 Digital Inputs

5.2 Digital Outputs

5.3 E-Stop Sequence

5.4 Fire Safety Sequence

6. HMI / GUI Specification

7. Hardware Architecture

7.1 ECU-1170-552A

7.2 Network Topology

7.3 Safety-Critical Paths

8. Network & IP Configuration

8.1 IP Addressing

8.2 Firewall / Port Rules

8.3 MQTT Topic Schema

8.4 MQTT Payload Format

9. BMS Protocol (CAN DBC)

9.1 Layer 2: BMU → EMS

9.2 Layer 1: LMU → BMU

9.3 CAN Bus Sizing

10. PCS Protocol (Modbus RTU V1.24)

10.1 Telemetry

10.2 Control

10.3 Protection

10.4 Fault Words

10.5 Boot/Shutdown

11. BTMS Protocol (Modbus RTU)

11.1 BTMS Telemetry

11.2 BTMS Control

11.3 BTMS Alarms

12. Energy Meter Protocol (Modbus RTU)

12.1 Meter Telemetry

13. DG Protocol (Modbus RTU)

13.1 DG Telemetry

13.2 DG Control

14. Solar PV Inverter Protocol (Modbus RTU)

14.1 PV Telemetry

15. Software Architecture

15.1 Config Files

15.2 Modules

15.3 RTDB

15.4 Modes & Algorithms

16. Certifications & Standards

17. Libraries & Dependencies

18. Development Roadmap

19. Scaling Examples

20. Per-Deployment Requirements

# 1. Product Overview

## 1.1 ReVx EMS Platform

ReVx EMS is a scalable Energy Management System for BESS ranging from residential (50 kWh) to containerized (6+ MWh). It manages BMS, PCS, BTMS (liquid or air-cooled), Fire Safety, metering (Schneider PM5xxx-class), DG (smart or relay-start), Solar PV inverters, and auxiliary sensors. Configuration-driven: cells/module (16S–108S), modules/rack (3–20), clusters, and all subsystems are YAML parameters. Single binary for all deployments.

## 1.2 Battery Hierarchy: Rack → Module → Cell

| Level | Component | Contains | Config | Range |
| --- | --- | --- | --- | --- |
| Cell | Li-ion cell | Single unit | N/A | 3.0–3.65V LFP / 2.8–4.2V NMC |
| Module | LMU | K cells series | bms.cells_per_module | 16S to 108S |
| Rack | Pack | M modules series | bms.modules_per_rack | 3 to 20 modules |
| Cluster | BMU + N racks | N racks parallel | bms.racks_per_cluster | 1 to 16 racks |
| System | Complete BESS | P clusters | system.cluster_count | 1 to 8+ clusters |

BMS comm: Layer 1 (LMU → BMU): per-module cell data via CAN 2.0B. Layer 2 (BMU → EMS): BMU aggregates all LMUs and sends pack-level data (SOC, V, I, faults) to EMS.

## 1.3 Scaling Range

| Parameter | Small | Medium | Large | Config |
| --- | --- | --- | --- | --- |
| Capacity | 50–215 kWh | 215–1,000 kWh | 1–6+ MWh | Derived |
| Clusters | 1 | 1–2 | 2–8+ | cluster_count |
| Modules/Rack | 3–5 | 5–10 | 10–20 | modules_per_rack |
| Cells/Module | 16S–32S | 16S–54S | 16S–108S | cells_per_module |
| Total Cells | 48–640 | 320–8,640 | 2,560–138,240+ | Derived |
| Data Points | ~200–800 | ~2,000–10,000 | ~10,000–100,000+ | Auto |

## 1.4 Key Design Principles

Configuration-Driven: All topology, devices, I/O in YAML. One binary for all.

Hot-Configurable: Alarms, control, schedules update without restart.

Protocol-Agnostic: YAML register maps / DBC files. Vendor swap = config change.

Safety-Independent: C process, direct GPIO, works if main app hangs.

Local-First: Autonomous offline. Cloud optional.

Multi-Source: Grid/Solar/BESS/DG priority by availability + time-of-day.

# 2. Architecture Diagrams

## 2.1 Battery Architecture

## 2.2 Software Architecture.

## 2.3 Hardware Architecture

# 3. EMS State Machine & Interlock Logic

## 3.1 System States

| State | Description | PCS State | Indicator | Exit Conditions |
| --- | --- | --- | --- | --- |
| INIT | System boot. RTDB allocation, config load, comm drivers starting, self-test. | OFF | All blink | Self-test pass → STANDBY; fail → FAULT |
| STANDBY | All comms active, BMS healthy, interlock conditions met. Awaiting operator command. | OFF (0x0291=0) | DO-3 Green ON | Operator Start (HMI/Cloud) → PRE-CHARGE |
| PRE-CHARGE | BMU closes pre-charge contactor. Bus voltage ramp monitored. Timeout = fault. | OFF | DO-3 Blink | Bus V within range → RUNNING; timeout/fault → FAULT |
| RUNNING | PCS ON, active power control. Normal charge/discharge per mode. | ON (0x0291=1) | DO-3 Green ON | Operator Stop → SHUTDOWN; fault → FAULT; E-Stop → E-STOP |
| SHUTDOWN | Graceful: ramp power to 0, PCS OFF, open contactors, save state. | 0x500E→0, 0x0291→0 | DO-3 OFF | Complete → STANDBY |
| FAULT | Recoverable fault detected. PCS stopped. Alarm active. Awaiting reset. | OFF | DO-4 Red ON | Fault clear + ACK → STANDBY; escalation → E-STOP |
| E-STOP | Emergency shutdown. Hardwired PCS trip (DO-5), ACDB trip (DO-0), siren (DO-6). | OFF (hardware) | DO-4 Red + DO-6 Siren | Physical reset + operator ACK → INIT |
| FIRE | Fire confirmed (Smoke+Heat). Extinguisher activated. All contactors open. | OFF (hardware) | DO-4 Red + DO-6 Siren | Site inspection + manual restart → INIT |

## 3.2 State Transition Diagram

INIT → STANDBY → PRE-CHARGE → RUNNING ↔ SHUTDOWN → STANDBY. Any state → FAULT (on recoverable fault). Any state → E-STOP (on E-Stop button DI-6+7). Any state → FIRE (on Smoke DI-3 + Heat DI-4). FAULT → STANDBY (on reset+ACK) or → E-STOP (on escalation). E-STOP / FIRE → INIT (on physical reset + inspection).

## 3.3 Interlock Matrix (PCS Start Permissives)

ALL of the following conditions must be TRUE before EMS transitions from STANDBY to PRE-CHARGE:

| # | Interlock Condition | Signal Source | Fail Action |
| --- | --- | --- | --- |
| IL-1 | BMS Heartbeat active (no timeout) | CAN BMU→EMS SOC_Message, 300ms cycle | Block start, alarm |
| IL-2 | BMU Operating State = IDLE or READY | BMU_Operating_State ≠ FAULT, OFF | Block start |
| IL-3 | SOC > cutoff_soc (e.g., >5% for discharge) | SOC from BMU | Block discharge |
| IL-4 | SOC < max_soc (e.g., <98% for charge) | SOC from BMU | Block charge |
| IL-5 | Cell V_min > undervoltage limit | Min_Max_Voltage V_min | Block start, alarm |
| IL-6 | Cell V_max < overvoltage limit | Min_Max_Voltage V_max | Block start, alarm |
| IL-7 | Cell T_max < overtemperature limit | Min_Max_Temperature T_max | Block start, alarm |
| IL-8 | Cell T_min > undertemperature limit | Min_Max_Temperature T_min | Block start, alarm |
| IL-9 | IMD insulation R_iso > minimum (e.g., >100 kΩ) | IMD_G_Isolation R_iso_Corrected | Block start, alarm |
| IL-10 | PCS fault words all clear | 0x1700–0x1707 = 0x0000 | Block start; must reset first |
| IL-11 | PCS grid state = STANDBY or STOP | 0x605C = 0 or 2 | Block start if already running |
| IL-12 | E-Stop NOT active | DI-6=LOW AND DI-7=HIGH | Block start, E-STOP state |
| IL-13 | Fire NOT active | DI-3=LOW AND DI-4=LOW | Block start, FIRE state |
| IL-14 | ACDB closed (grid connected) — for on-grid mode | DI-0=HIGH | Block on-grid start |
| IL-15 | Flood NOT active | DI-1=LOW | Block start (configurable) |
| IL-16 | BTMS within operating range (if liquid-cooled) | BTMS coolant_temp < max | Block start, alarm |
| IL-17 | PCS comm healthy (Modbus response within timeout) | Modbus response < 1648 timeout | Block start, alarm |

## 3.4 Runtime Protection Actions (RUNNING state)

| Condition | Detection | Action | Recovery |
| --- | --- | --- | --- |
| SOC at L1 (e.g., 15%) | SOC from BMU | Derate power to 50% | SOC rises above L1+hysteresis |
| SOC at L2 (e.g., 10%) | SOC from BMU | Derate to 20% | SOC rises above L2+hysteresis |
| SOC at cutoff (e.g., 5%) | SOC from BMU | Stop discharge, → SHUTDOWN | Operator re-start after charge |
| Cell V near limit | V_max or V_min approaching threshold | Derate proportionally | V returns to safe range |
| Cell T high | T_max > warning threshold | Derate + BTMS escalation | T drops below threshold |
| PCS fault word bit set | 0x1700–0x1707 any non-zero | Stop PCS, → FAULT | Fault reset (0x5064) |
| BMS heartbeat lost | No SOC_Message for >1s | Stop PCS, → FAULT | Heartbeat restored + ACK |
| PCS comm lost | Modbus timeout (0x1648) | Stop PCS, → FAULT | Comm restored + ACK |
| E-Stop pressed | DI-6 rise + DI-7 fall | Hardwired trip, → E-STOP | Physical reset |
| Fire detected | DI-3 + DI-4 both HIGH | Hardwired trip + extinguisher, → FIRE | Site inspection |

# 4. Power Source Priority Logic

## 4.1 DAY Mode

Solar is P1 when available. Grid supplements. BESS for peak shaving. DG is last resort.

| Grid | Solar | BESS | DG | P1 | P2 | P3 | P4 | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| NO | NO | NO | NO | — | — | — | — | BLACKOUT |
| NO | NO | NO | YES | DG | — | — | — |  |
| NO | NO | YES | NO | BESS | — | — | — |  |
| NO | NO | YES | YES | BESS | DG | — | — |  |
| NO | YES | NO | NO | Solar | — | — | — |  |
| NO | YES | NO | YES | Solar | DG | — | — |  |
| NO | YES | YES | NO | Solar | BESS | — | — |  |
| NO | YES | YES | YES | Solar | BESS | DG | — | Grid N/A |
| YES | NO | NO | NO | Grid | — | — | — |  |
| YES | NO | NO | YES | Grid | DG | — | — |  |
| YES | NO | YES | NO | Grid | BESS | — | — |  |
| YES | NO | YES | YES | Grid | BESS | DG | — | Solar N/A |
| YES | YES | NO | NO | Solar | Grid | — | — |  |
| YES | YES | NO | YES | Solar | Grid | DG | — |  |
| YES | YES | YES | NO | Solar | Grid | BESS | — |  |
| YES | YES | YES | YES | Solar | Grid | BESS | DG | All available |

## 4.2 NIGHT Mode

| Grid | BESS | DG | P1 | P2 | P3 | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| NO | NO | NO | — | — | — | BLACKOUT |
| NO | NO | YES | DG | — | — |  |
| NO | YES | NO | BESS | — | — |  |
| NO | YES | YES | BESS | DG | — | Grid N/A |
| YES | NO | NO | Grid | — | — |  |
| YES | NO | YES | Grid | DG | — |  |
| YES | YES | NO | Grid | BESS | — |  |
| YES | YES | YES | Grid | BESS | DG | All available |

## 4.3 Source Manager Implementation

1 Hz loop: read availability → day/night (sunrise/sunset config or irradiance) → select per table → PCS setpoint (0x500E), DG start/stop (Modbus), ACDB (DO-0).

# 5. I/O Subsystems & Signal List

## 5.1 Digital Inputs (DI)

| DI | Subsystem | Signal | Active | Description |
| --- | --- | --- | --- | --- |
| DI-0 | ACDB | Aux Status | High=Closed | ACDB contactor feedback |
| DI-1 | Flood Sensor | Status | High=Flood | Water ingress |
| DI-2 | Limit Switch | Status | High=Open | Door/panel access |
| DI-3 | Smoke Sensor | Status | High=Smoke | Fire detection (FSS) |
| DI-4 | Heat Detector | Status | High=Heat | Thermal anomaly (FSS) |
| DI-5 | Fire Ext. | Status | High=Discharged | Suppression feedback |
| DI-6 | EM OFF PB | NO contact | High=Pressed | E-Stop normally open |
| DI-7 | EM OFF PB | NC contact | Low=Pressed | E-Stop normally closed (dual-channel) |

## 5.2 Digital Outputs (DO)

| DO | Subsystem | Signal | Active | Description |
| --- | --- | --- | --- | --- |
| DO-0 | ACDB | Shunt Trip | High=Trip | Grid disconnect |
| DO-1 | Fire Ext. | Drive | High=Activate | Fire suppression |
| DO-2 | Warning | Indicator | High=ON | Yellow lamp (E_W) |
| DO-3 | Running | Indicator | High=ON | Green lamp (PCS Run) |
| DO-4 | Fault | Indicator | High=ON | Red lamp (A_P/P_P) |
| DO-5 | PCS | Em Stop | High=Stop | PCS emergency stop (hardware) |
| DO-6 | Siren | Drive | High=ON | Audible alarm |
| DO-7 | Reserved | — | — | Spare |

## 5.3 E-Stop Sequence

DI-6 rises + DI-7 falls (dual-channel) → Safety Manager (<100ms)

DO-5 HIGH (PCS Em Stop), DO-0 HIGH (ACDB trip)

DO-6 HIGH (Siren), DO-4 HIGH (Fault lamp)

Modbus 0x0291→0 backup. State → E-STOP. Recovery: physical reset + ACK.

## 5.4 Fire Safety Sequence

DI-3 + DI-4 (dual confirm) → DO-1 (extinguisher), DO-5 (PCS stop), DO-0 (ACDB)

DO-6 (siren), DO-4 (fault). DI-5 monitors discharge. CAN: open all contactors. Cloud alert.

# 6. HMI / GUI Specification

| # | Screen | Key Data | Actions | Refresh |
| --- | --- | --- | --- | --- |
| 1 | Dashboard | Grid/Solar/Battery/DG kW, SOC%, AC Bus, Status tiles, 3-phase, 24h chart, Alerts, Source priority, EMS State | Mode, Start/Stop, E-OFF | 1s |
| 2 | Cluster | Cluster V/I, Rack cards: SOC%, SOH%, V, Status, Max/Min Cell V/T | Tap rack | 1s |
| 3 | Rack Detail | Pack V/I, BMS State, SOC gauge, Cell V by Module:Cell, Cycle Count, SOH | Search, Sort | 1s |
| 4 | Cell Details | Per-cell V/T grid (16S–108S × 3–20 mod). Bar chart. | Toggle V/T | 500ms |
| 5 | Alarms | Active/Cleared/NACK. Filters. ACK Status. | ACK ALL | Event |
| 6 | Settings–Mode | Schedule/On Grid/Off Grid. Times, Power, Source priority. | Edit, Stop | On-demand |
| 7 | Settings–System | CAN/RS485/IP config. DI/DO live status. BTMS/Meter/DG status. | Edit | On-demand |

# 7. Hardware Architecture

## 7.1 ECU-1170-552A

| Component | Specification | Usage |
| --- | --- | --- |
| Processor | TI AM6548: 4×A53 + 2×R5 | EMS + safety |
| RAM / Storage | 4GB DDR4 / 64GB eMMC + 256–512GB SSD | RTDB + telemetry logs |
| CAN | 2× CAN 2.0B isolated | BMS clusters |
| Serial | 4× RS-485 isolated | PCS, Meter, BTMS, DG/PV |
| Ethernet | 2× GbE | LAN + WAN |
| Digital I/O | 8 DI + 8 DO | Section 5 signal list |
| Display | HDMI | 10" touch |
| Temp / Certs | -40°C to +70°C, CE/FCC/UL | Industrial |

## 7.2 Network Topology

| Interface | Device | Protocol | Config |
| --- | --- | --- | --- |
| CAN0/CAN1 | BMU Cluster 1/2 | DBC L2 (BMU→EMS) | bitrate, dbc_file |
| RS485-1 | PCS Inverter | Modbus RTU 9600/8N1 | slave_id 1 |
| RS485-2 | Energy Meter | Modbus RTU 9600/8N1 | slave_id 2 |
| RS485-3 | BTMS Controller | Modbus RTU 9600/8N1 | slave_id 3 |
| RS485-4 | DG / PV Inverter | Modbus RTU 9600/8N1 | slave_id 4/5 |
| ETH0 (LAN) | PCS TCP, HMI, Meter | TCP, HTTP/WS | 192.168.1.x |
| ETH1 (WAN) | Cloud, NTP | MQTT/TLS, NTP | DHCP/static |
| DI/DO | Section 5 | GPIO | gpio_config.yaml |

## 7.3 Safety-Critical Hardware Paths

| Trigger | Input | HW Action | SW Action |
| --- | --- | --- | --- |
| E-Stop | DI-6+7 | DO-5+DO-0 | Log, siren, fault lamp |
| Fire | DI-3+4 | DO-1 extinguisher | PCS stop, ACDB, cloud |
| BMS Critical | CAN fault | BMU contactors (HVIL) | Log, PCS down, alarm |
| Flood | DI-1 | None | Alarm, optional shutdown |

# 8. Network & IP Configuration

## 8.1 IP Addressing Scheme

| Interface | Subnet | Device | IP Address | Notes |
| --- | --- | --- | --- | --- |
| ETH0 (LAN) | 192.168.1.0/24 | EMS Controller | 192.168.1.1 | Static. Gateway for LAN devices. |
|  |  | PCS (Modbus TCP) | 192.168.1.10 | Static. Port 502. |
|  |  | HMI Touchscreen | 192.168.1.1:8080 | EMS serves HMI webapp. |
|  |  | Energy Meter (if TCP) | 192.168.1.20 | Optional TCP meter. |
|  |  | BTMS (if TCP) | 192.168.1.30 | Optional TCP BTMS. |
|  |  | Operator Laptop | 192.168.1.100–199 | DHCP range for maintenance. |
| ETH1 (WAN) | Site LAN / LTE | EMS Controller | DHCP or static | Assigned by site IT / LTE carrier. |
|  |  | Cloud MQTT Broker | Broker URL (cloud) | TLS on port 8883. |
|  |  | NTP Server | pool.ntp.org or site NTP | Port 123 UDP. |

## 8.2 Firewall / Port Rules

| Port | Protocol | Direction | Interface | Service | Notes |
| --- | --- | --- | --- | --- | --- |
| 502 | TCP | LAN only | ETH0 | Modbus TCP (PCS) | EMS → PCS. Block from WAN. |
| 8080 | TCP | LAN only | ETH0 | HMI WebSocket/HTTP | EMS serves React SPA. |
| 8883 | TCP | Outbound | ETH1 | MQTT TLS | EMS → Cloud broker. Mutual TLS. |
| 123 | UDP | Outbound | ETH1 | NTP | Time sync. |
| 22 | TCP | LAN only | ETH0 | SSH | Maintenance access. Key-based auth only. |
| 53 | UDP | Outbound | ETH1 | DNS | Name resolution for MQTT broker. |
| * | * | Inbound | ETH1 | ALL | BLOCKED by default. No inbound WAN. |

## 8.3 MQTT Topic Schema

All MQTT topics follow the hierarchy: revx/{site_id}/{category}/{subsystem}/{...}

| Topic Pattern | QoS | Direction | Payload | Rate |
| --- | --- | --- | --- | --- |
| revx/{site}/telemetry/bms/cluster/{C}/rack/{R} | 0 | EMS→Cloud | SOC, V, I, state, temps | 1–60s config |
| revx/{site}/telemetry/bms/cluster/{C}/rack/{R}/cells | 0 | EMS→Cloud | All cell V array | 10–60s config |
| revx/{site}/telemetry/pcs | 0 | EMS→Cloud | AC V/I/P/Q, DC V/I, temps, state | 1–10s |
| revx/{site}/telemetry/btms | 0 | EMS→Cloud | Temps, mode, fan/pump, status | 5–30s |
| revx/{site}/telemetry/meter | 0 | EMS→Cloud | 3-phase V/I/P/Q/PF, kWh | 5–30s |
| revx/{site}/telemetry/dg | 0 | EMS→Cloud | Run status, V/I/P, fuel, hours | 5–30s |
| revx/{site}/telemetry/pv | 0 | EMS→Cloud | DC/AC P, energy, status | 5–30s |
| revx/{site}/telemetry/gpio | 0 | EMS→Cloud | DI/DO states | On change + 60s heartbeat |
| revx/{site}/telemetry/ems | 0 | EMS→Cloud | EMS state, mode, setpoint, source priority | 1–10s |
| revx/{site}/alarms | 1 | EMS→Cloud | Alarm event JSON (IEC 62682) | On event |
| revx/{site}/events | 1 | EMS→Cloud | State transitions, operator actions | On event |
| revx/{site}/command/pcs | 2 | Cloud→EMS | Power setpoint, on/off, mode | On demand |
| revx/{site}/command/dg | 2 | Cloud→EMS | DG start/stop | On demand |
| revx/{site}/command/config | 2 | Cloud→EMS | Config update (schedule, alarms, etc.) | On demand |
| revx/{site}/command/ota | 2 | Cloud→EMS | Firmware update trigger | On demand |
| revx/{site}/status/ota | 1 | EMS→Cloud | OTA progress, result | On event |

## 8.4 MQTT Payload Format

All payloads are JSON. Example telemetry: {"ts":"2026-02-25T14:30:00Z", "site":"revx-001", "soc":72.5, "pack_v":512.8, "pack_i":-45.2, "state":"RUNNING", "mode":"schedule"}. Alarm: {"ts":..., "id":"ALM-0042", "source":"BMS", "signal":"cell_v_max", "value":3.68, "threshold":3.65, "priority":"A_P", "state":"ACTIVE"}. Commands: {"action":"set_power", "value":-200, "unit":"kW_x10"}.

# 9. BMS Communication Protocol (CAN DBC)

Layer 1 (LMU → BMU): Per-module cell data. Internal to BMS.

Layer 2 (BMU → EMS): BMU aggregates LMUs, sends pack-level data. Primary EMS interface.

Reference DBC: V_0–V_159, T_0–T_39. Actual counts from config. Extended DBC for >40 cells.

## 9.1 Layer 2: BMU → EMS (Primary)

| CAN ID | Message | Cycle | Key Signals |
| --- | --- | --- | --- |
| 0x98FF0003 | SOC_Message | 300ms | SOC (0.5%), Charge/Discharge Limit (0.125A), BMU_State, Heartbeat |
| 0x98FF0103 | Pack_Voltage_Current | 300ms | Pack_V (0.0625V), Pack_I (0.125A), Contactor status |
| 0x98FF0203 | Min_Max_Voltage | 300ms | V_min, V_max (0.000122V), V_min_ID, V_max_ID |
| 0x98FF0303 | Min_Max_Temperature | 300ms | T_min, T_max (0.015625°C), T_min_ID, T_max_ID |
| 0x98FF0403 | DTC_Accommodation | 300ms | Active_Fault_1..8 |
| 0x98FF0503 | Pack_Status | 300ms | Rack_ID, MCCB, Fuse, Fan, Watchdog |
| 0x98FF0803 | Pack_Info | 1000ms | SOH (0.5%), Cycle_Count, Delta_V, Delta_T |
| 0x98FF2003.. | Cell_Voltages_1..28+ | 2000ms | V_0–V_159 (4/msg, up to 160 cells) |
| 0x98FF8003.. | Cell_Temps_1..10 | 2000ms | T_0–T_39 (4/msg, up to 40 sensors) |
| 0x98FF0603/07 | Hw/Fw_Version | 3000ms | 8-byte version strings |
| 0x98FF0903 | Time_Date | 1000ms | Timestamp, LMU_State |

## 9.2 Layer 1: LMU → BMU (Reference)

| Group | Signals | Notes |
| --- | --- | --- |
| Cell V/T | V_0..V_159, T_0..T_39 | Per-module, aggregated by BMU |
| IMD | R_iso (0–37.5kΩ), Status, Alarms, Quality | Insulation monitoring |
| IMD Voltage | HV, HVneg_Earth, HVpos_Earth | HV vs earth |
| Wire Diag | V_Wire_Open, T_Wire_Open/Short | Wiring faults |
| Cell Balance | CB_0..CB_7 | Active balancing |
| Diagnostics | Delta_V, Delta_T, OBT, HVIL, Fuse | Rack health |
| Contactors | Main+/−, PreCharge, Charge, MCU | Control/feedback |

## 9.3 CAN Bus Sizing

| Config | Cells | V Msgs | Frames/s (8 racks) | Bus |
| --- | --- | --- | --- | --- |
| 16S×3mod=48 | 48 | 12 | 120 | CAN 2.0B |
| 32S×5mod=160 | 160 | 40 | 360 | CAN 2.0B |
| 54S×10mod=540 | 540 | 135 | 1,192 | CAN FD |
| 108S×20mod=2160 | 2160 | 540 | 4,480 | Multi FD/ETH |

# 10. PCS Communication Protocol (Modbus RTU V1.24)

RS485, FC03/FC06, 9600/8N1, 16 regs/read max. Slave ID configurable.

## 10.1 Telemetry (Read-Only)

| Address | Signal | Scale | Notes |
| --- | --- | --- | --- |
| 0x6020–0x6022 | AC line V (AB,BC,CA) | V×10 |  |
| 0x6023–0x6025 | AC phase V (A,B,C) | V×10 |  |
| 0x6026–0x6028 | AC phase I (A,B,C) | A×10 |  |
| 0x602C | Grid frequency | Hz×100 | 5000=50Hz |
| 0x6030–0x6032 | Per-phase P | kW×10 | +dchg |
| 0x6039–603B | Total P/Q/S | kW/kVAr/kVA×10 |  |
| 0x603C | Power factor | ×100 |  |
| 0x6050–0x6052 | Bus V (total/pos/neg) | V×10 |  |
| 0x6053/6054 | Battery V / I | V/A×10 |  |
| 0x6055 | DC power | kW×10 |  |
| 0x6057 | Working condition | bitfield |  |
| 0x6058–605A | PCS temps | °C×10 | IGBT/ambient/inductance |
| 0x605C | Grid state | enum | 0–6 |
| 0x6010–601F | Energy counters | kWh | 8 U32 pairs |

## 10.2 Control (R/W)

| Address | Signal | Scale | Notes |
| --- | --- | --- | --- |
| 0x500E | Active power setpoint | kW×10 | PRIMARY. +dchg −chg |
| 0x500F | Reactive power | kVAr×10 |  |
| 0x0291 | Power on/off | 1 | 1=ON, wait 10s |
| 0x5064 | Fault reset | 1 | Write 1 |
| 0x5066 | Off-grid mode | 1 | 1=offgrid |
| 0x5078/5079 | Max chg/dchg P | kW×10 |  |
| 0x163F/1640 | Max chg/dchg I | A×10 | DC limit |

## 10.3 Protection (R/W)

| Address | Signal | Scale |
| --- | --- | --- |
| 0x1600/1601 | AC V OV/UV | V×10 |
| 0x1604/1605 | Grid freq OV/UV | Hz×100 |
| 0x1633/1634 | Battery V OV/UV | V×10 |
| 0x1641 | DC overcurrent | A×10 |
| 0x1648 | Comm timeout | seconds |

## 10.4 Fault Words (0x1700–0x1707)

| Reg | Name | Key Bits |
| --- | --- | --- |
| 0x1700 | HW 1 | EPO, IGBT OCP, Bus OV |
| 0x1701 | HW 2 | PSU, Fan, OT, Fire |
| 0x1702 | Grid | Phase OV/UV, Freq, Phase seq, OC |
| 0x1703 | Bus | Pre-charge, Run OV/UV, Batt, DC OC |
| 0x1704 | AC Cap | Timeout, Leakage, Mismatch |
| 0x1705 | System | RAM, EEPROM, CAN, BMS/EMS comm |
| 0x1706 | Switch | Relay faults. CRITICAL. |
| 0x1707 | Other | Inv OV/UV, Island, Short circuit |

## 10.5 Boot/Shutdown

Charge: 0x0291←1 (10s), 0x500E←neg. Discharge: positive. Stop: 0x500E←0, 0x0291←0. Reset: 0x5064←1.

# 11. BTMS Protocol (Modbus RTU)

RS485, 9600/8N1. Configurable for liquid-cooled (chiller + coolant pump) or air-cooled (fans + optional AC). Slave ID from devices_config.yaml.

## 11.1 BTMS Telemetry (Read-Only)

| Address | Signal | Type | Scale | Notes |
| --- | --- | --- | --- | --- |
| 0x0000 | Coolant inlet temperature | I16 | °C ×10 | Liquid-cooled: coolant entering battery rack |
| 0x0001 | Coolant outlet temperature | I16 | °C ×10 | Liquid-cooled: coolant leaving battery rack |
| 0x0002 | Coolant flow rate | U16 | L/min ×10 | Liquid-cooled: pump flow sensor |
| 0x0003 | Coolant pressure | U16 | kPa ×10 | Liquid-cooled: system pressure |
| 0x0004 | Ambient temperature (inside) | I16 | °C ×10 | Container internal air temp |
| 0x0005 | Ambient temperature (outside) | I16 | °C ×10 | External ambient |
| 0x0006 | Humidity (inside) | U16 | % ×10 | Container RH |
| 0x0007 | Compressor status | U16 | enum | 0=OFF, 1=Heating, 2=Cooling, 3=Dehumidify, 4=Fault |
| 0x0008 | Pump 1 status | U16 | enum | 0=OFF, 1=ON, 2=Fault. Liquid-cooled only. |
| 0x0009 | Pump 2 status | U16 | enum | 0=OFF, 1=ON, 2=Fault. Redundant pump. |
| 0x000A | Fan 1 speed | U16 | RPM | Air-cooled: intake fan |
| 0x000B | Fan 2 speed | U16 | RPM | Air-cooled: exhaust fan |
| 0x000C | Fan 3 speed (condenser) | U16 | RPM | Condenser fan for chiller |
| 0x000D | Heater status | U16 | enum | 0=OFF, 1=ON, 2=Fault. For low-temp operation. |
| 0x000E | System operating mode | U16 | enum | 0=Standby, 1=Cooling, 2=Heating, 3=Dehumidify, 4=Auto, 5=Fault |
| 0x000F | Power consumption | U16 | W ×10 | BTMS total electrical draw |
| 0x0010 | Refrigerant pressure (high) | U16 | kPa ×10 | Liquid-cooled: chiller high-side |
| 0x0011 | Refrigerant pressure (low) | U16 | kPa ×10 | Liquid-cooled: chiller low-side |
| 0x0012 | Coolant level | U16 | % ×10 | Liquid-cooled: reservoir level |
| 0x0013 | Run hours (compressor) | U32 | hours | Maintenance tracking |
| 0x0015 | Run hours (pumps) | U32 | hours | Maintenance tracking |
| 0x0017 | Firmware version | U16 |  | Major.Minor encoded |

## 11.2 BTMS Control (R/W)

| Address | Signal | Type | Scale | Notes |
| --- | --- | --- | --- | --- |
| 0x0100 | Cooling setpoint temperature | I16 | °C ×10 | Target coolant/air temp for cooling mode |
| 0x0101 | Heating setpoint temperature | I16 | °C ×10 | Target for heating mode (low-temp) |
| 0x0102 | Operating mode command | U16 | enum | 0=Standby, 1=Cooling, 2=Heating, 3=Dehumidify, 4=Auto |
| 0x0103 | Fan speed override | U16 | % ×10 | 0=Auto, 1–1000=10–100% manual speed |
| 0x0104 | Pump speed override | U16 | % ×10 | 0=Auto, 1–1000. Liquid-cooled only. |
| 0x0105 | Fault reset | U16 | 1 | Write 1 to clear faults |
| 0x0106 | Emergency stop | U16 | 1 | Write 1: all outputs OFF immediately |
| 0x0107 | Dehumidification enable | U16 | 1 | 0=disabled, 1=enabled |
| 0x0108 | High temp alarm threshold | I16 | °C ×10 | Configurable per deployment |
| 0x0109 | Low temp alarm threshold | I16 | °C ×10 | Configurable per deployment |

## 11.3 BTMS Alarms (Read-Only)

| Address | Signal | Bits | Description |
| --- | --- | --- | --- |
| 0x0200 | Alarm word 1 | bit0: Coolant OT, bit1: Coolant UT, bit2: Ambient OT, bit3: Ambient UT, bit4: Humidity high, bit5: Coolant flow low, bit6: Coolant pressure high, bit7: Coolant pressure low | Temperature and environmental |
| 0x0201 | Alarm word 2 | bit0: Pump 1 fault, bit1: Pump 2 fault, bit2: Fan 1 fault, bit3: Fan 2 fault, bit4: Compressor fault, bit5: Heater fault, bit6: Refrigerant low, bit7: Coolant level low | Equipment faults |
| 0x0202 | Alarm word 3 | bit0: Comm loss, bit1: Sensor fault (temp), bit2: Sensor fault (flow), bit3: Sensor fault (pressure), bit4: Power supply fault, bit5: Emergency stop active | System faults |

# 12. Energy Meter Protocol (Modbus RTU)

Based on Schneider PM5xxx family register map. RS485, 9600/8N1. This is the revenue-grade measurement (source of truth for billing/grid compliance, independent of PCS self-measurement).

## 12.1 Meter Telemetry (Read-Only)

| Address | Signal | Type | Scale | Notes |
| --- | --- | --- | --- | --- |
| 0x0BCD | Phase A voltage (L-N) | F32 | V | IEEE 754 float (2 regs) |
| 0x0BCF | Phase B voltage (L-N) | F32 | V |  |
| 0x0BD1 | Phase C voltage (L-N) | F32 | V |  |
| 0x0BD3 | Phase A-B voltage (L-L) | F32 | V |  |
| 0x0BD5 | Phase B-C voltage (L-L) | F32 | V |  |
| 0x0BD7 | Phase C-A voltage (L-L) | F32 | V |  |
| 0x0BB7 | Phase A current | F32 | A |  |
| 0x0BB9 | Phase B current | F32 | A |  |
| 0x0BBB | Phase C current | F32 | A |  |
| 0x0BBD | Neutral current | F32 | A |  |
| 0x0BED | Phase A active power | F32 | kW | + = import (from grid) |
| 0x0BEF | Phase B active power | F32 | kW |  |
| 0x0BF1 | Phase C active power | F32 | kW |  |
| 0x0BF3 | Total active power | F32 | kW | + import, − export |
| 0x0BF5 | Phase A reactive power | F32 | kVAr |  |
| 0x0BF7 | Phase B reactive power | F32 | kVAr |  |
| 0x0BF9 | Phase C reactive power | F32 | kVAr |  |
| 0x0BFB | Total reactive power | F32 | kVAr |  |
| 0x0BFD | Phase A apparent power | F32 | kVA |  |
| 0x0C03 | Total apparent power | F32 | kVA |  |
| 0x0C05 | Total power factor | F32 | — | + = lagging, − = leading |
| 0x0C07 | Frequency | F32 | Hz |  |
| 0x0C83 | Total active energy import | I64 | kWh | Accumulated. 4 registers. |
| 0x0C87 | Total active energy export | I64 | kWh | Accumulated. |
| 0x0C8B | Total reactive energy import | I64 | kVArh |  |
| 0x0C8F | Total reactive energy export | I64 | kVArh |  |
| 0x0C9B | Demand active power (current) | F32 | kW | Rolling demand window |
| 0x0C9D | Demand active power (peak) | F32 | kW | Maximum demand since reset |

Schneider PM5xxx uses 32-bit IEEE 754 floats (2 consecutive Modbus registers per value). Read with FC03, 2 registers at a time. 64-bit energy accumulators use 4 registers. Address offsets may vary by PM5xxx sub-model; verify against specific datasheet.

# 13. DG Protocol (Modbus RTU)

Configurable for Smart controller (DeepSea DSE7320 / ComAp InteliLite style with full telemetry) or Simple relay-start (limited to start/stop + run status via DI/DO). RS485, 9600/8N1.

## 13.1 DG Telemetry (Read-Only) — Smart Controller

| Address | Signal | Type | Scale | Notes |
| --- | --- | --- | --- | --- |
| 0x0000 | Generator status | U16 | enum | 0=Stopped, 1=Pre-heat, 2=Cranking, 3=Running, 4=Cooling down, 5=Fault |
| 0x0001 | Engine RPM | U16 | RPM |  |
| 0x0002 | Oil pressure | U16 | kPa |  |
| 0x0003 | Coolant temperature | I16 | °C ×10 | Engine coolant |
| 0x0004 | Battery voltage (starter) | U16 | V ×10 | 12V/24V starter battery |
| 0x0005 | Fuel level | U16 | % ×10 | 0–1000 = 0–100% |
| 0x0006 | Run hours | U32 | hours | Total engine hours. 2 registers. |
| 0x0008 | Output voltage L1-N | U16 | V ×10 |  |
| 0x0009 | Output voltage L2-N | U16 | V ×10 |  |
| 0x000A | Output voltage L3-N | U16 | V ×10 |  |
| 0x000B | Output current L1 | U16 | A ×10 |  |
| 0x000C | Output current L2 | U16 | A ×10 |  |
| 0x000D | Output current L3 | U16 | A ×10 |  |
| 0x000E | Output frequency | U16 | Hz ×100 |  |
| 0x000F | Output active power | I16 | kW ×10 | Total 3-phase |
| 0x0010 | Output power factor | I16 | ×100 |  |
| 0x0011 | Fuel consumption rate | U16 | L/hr ×10 | If sensor available |
| 0x0012 | Total energy generated | U32 | kWh | Accumulated. 2 registers. |
| 0x0014 | Exhaust temperature | I16 | °C ×10 | If sensor available |

## 13.2 DG Control (R/W) — Smart Controller

| Address | Signal | Type | Scale | Notes |
| --- | --- | --- | --- | --- |
| 0x0100 | Start/Stop command | U16 | enum | 0=Stop, 1=Start, 2=Auto (EMS-managed) |
| 0x0101 | Fault reset | U16 | 1 | Write 1 to clear faults |
| 0x0102 | Load transfer command | U16 | 1 | 1=Close DG breaker, 0=Open. For ATS integration. |
| 0x0103 | Governor setpoint | U16 | Hz ×100 | Frequency target (default 5000=50Hz) |

## 13.3 DG Alarms (Read-Only)

| Address | Alarm Word | Bits |
| --- | --- | --- |
| 0x0200 | Engine alarms | bit0: Low oil pressure, bit1: High coolant temp, bit2: Overspeed, bit3: Underspeed, bit4: Low fuel, bit5: Crank fail, bit6: Low battery, bit7: High battery |
| 0x0201 | Electrical alarms | bit0: Output OV, bit1: Output UV, bit2: Output OC, bit3: Over-freq, bit4: Under-freq, bit5: Reverse power, bit6: Earth fault |
| 0x0202 | System alarms | bit0: Emergency stop, bit1: Maintenance due, bit2: Comm loss, bit3: Sensor fault, bit4: Charger fault |

### 13.4 Simple Relay-Start DG (GPIO Fallback)

For DG without Modbus: DO-7 (spare) drives start relay. DI reads run status (aux contact on DG breaker). No telemetry — only start/stop + run feedback. Configured in gpio_config.yaml as dg_start_output and dg_run_input.

# 14. Solar PV Inverter Protocol (Modbus RTU)

Generic register map for grid-tied PV inverters (compatible with Sungrow, Huawei, GoodWe, Fronius). RS485, 9600/8N1.

## 14.1 PV Telemetry (Read-Only)

| Address | Signal | Type | Scale | Notes |
| --- | --- | --- | --- | --- |
| 0x0000 | Inverter status | U16 | enum | 0=Standby, 1=Running, 2=Fault, 3=Shutdown |
| 0x0001 | DC input voltage (string 1) | U16 | V ×10 | PV string 1 |
| 0x0002 | DC input current (string 1) | U16 | A ×10 |  |
| 0x0003 | DC input power (string 1) | U16 | W |  |
| 0x0004 | DC input voltage (string 2) | U16 | V ×10 | PV string 2 (if dual MPPT) |
| 0x0005 | DC input current (string 2) | U16 | A ×10 |  |
| 0x0006 | DC input power (string 2) | U16 | W |  |
| 0x0007 | Total DC power | U16 | W | Sum of all strings |
| 0x0008 | AC output voltage (L1) | U16 | V ×10 |  |
| 0x0009 | AC output voltage (L2) | U16 | V ×10 |  |
| 0x000A | AC output voltage (L3) | U16 | V ×10 |  |
| 0x000B | AC output current (L1) | U16 | A ×10 |  |
| 0x000C | AC output current (L2) | U16 | A ×10 |  |
| 0x000D | AC output current (L3) | U16 | A ×10 |  |
| 0x000E | AC output frequency | U16 | Hz ×100 |  |
| 0x000F | AC active power (total) | I16 | W |  |
| 0x0010 | AC reactive power | I16 | VAr |  |
| 0x0011 | Power factor | I16 | ×100 |  |
| 0x0012 | Inverter temperature | I16 | °C ×10 | Internal heatsink |
| 0x0013 | Daily energy | U32 | Wh | Today’s generation. 2 regs. |
| 0x0015 | Total energy | U32 | kWh | Lifetime accumulated. 2 regs. |
| 0x0017 | Irradiance | U16 | W/m² | If sensor connected. Used for Day/Night detection. |
| 0x0018 | Fault code | U16 | bitfield | Vendor-specific fault bits |

Address offsets are generic. Each PV vendor has different register maps. Create pv_vendor.yaml per deployment with actual addresses mapped to these logical signal names.

# 15. Software Architecture

## 15.1 Configuration Files

| File | Key Parameters | Hot |
| --- | --- | --- |
| system_config.yaml | cluster_count, racks_per_cluster, modules_per_rack (3–20), cells_per_module (16–108) | No |
| bms_config.yaml | can_interface, bitrate, dbc_file (L1/L2) | No |
| pcs_config.yaml | protocol, port/baud, slave_id, register_map | No |
| btms_config.yaml | protocol, port/baud, slave_id, cooling_type (liquid/air), setpoints | No |
| meter_config.yaml | protocol, port/baud, slave_id, register_map (pm5xxx.yaml), data_type (float) | No |
| dg_config.yaml | type (smart/relay), protocol/port/baud, slave_id, register_map, auto_start_soc | No |
| pv_config.yaml | protocol, port/baud, slave_id, register_map (vendor.yaml), string_count | No |
| control_config.yaml | soc_levels, derating, ramp_rate, source_priority (day/night) | Yes |
| alarms_config.yaml | Per-signal thresholds, hysteresis, delay | Yes |
| schedule_config.yaml | charge/discharge windows, 96-pt curve, mode | Yes |
| cloud_config.yaml | broker_url, topic_prefix (revx/{site}), telemetry_intervals, auth | No |
| network_config.yaml | eth0_ip, eth1_mode, firewall_rules, ntp_server | No |
| gpio_config.yaml | DI/DO pin map per Section 5 | No |
| hmi_config.yaml | resolution, branding, refresh_rates | Yes |

## 15.2 Module Inventory

| Module | Lang | P | Description |
| --- | --- | --- | --- |
| comm_manager | C/C++/Py | P0 | CAN (cantools DBC BMU→EMS), Modbus TCP/RTU (PCS+BTMS+Meter+DG+PV), GPIO. Health+reconnect. |
| control_manager | Py/C | P0 | 1 Hz: state machine (Sec 3) → source priority (Sec 4) → interlock check → algorithm → PCS/DG/ACDB. |
| data_manager | C/Py | P0 | RTDB: /bms/..., /pcs/..., /btms/..., /meter/..., /dg/..., /pv/..., /gpio/..., /control/... |
| alarm_manager | Py | P0 | 3-tier. IEC 62682. Maps to DO-2/3/4 indicators. |
| safety_manager | C | P0 | E-Stop (DI-6+7), Fire (DI-3+4), Flood (DI-1). <100ms. HW watchdog. |
| logger | C++/Py | P1 | Parquet 1Hz. DuckDB. JSONL events. |
| cloud_manager | Py | P1 | MQTT per Section 8.3 topic schema. Offline buffer. |
| hmi_server | Py/React | P1 | 7 screens. WebSocket 1s push. |
| scheduler | Py | P1 | Windows, 96-pt curves. |
| config_manager | Py | P2 | YAML validation, versioned, backup. |
| ota_manager | Py | P2 | A/B partition, signature, rollback. |
| diagnostics | Py | P2 | SOH, PCS efficiency, BTMS performance, comm health. |

## 15.3 RTDB Namespace

| Path | Type | Source |
| --- | --- | --- |
| /bms/cluster[C]/rack[R]/module[M]/cell_voltage[K] | U16 mV | BMU L2 |
| /bms/cluster[C]/rack[R]/soc | U16 0.1% | BMU L2 |
| /bms/cluster[C]/rack[R]/bms_state | Enum | BMU L2 |
| /pcs/active_power | I16 0.1kW | PCS 0x6039 |
| /pcs/fault_words[0..7] | U16 | PCS 0x1700 |
| /btms/coolant_inlet_temp | I16 0.1°C | BTMS 0x0000 |
| /btms/mode | Enum | BTMS 0x000E |
| /btms/alarm_words[0..2] | U16 | BTMS 0x0200 |
| /meter/total_active_power | F32 kW | Meter 0x0BF3 |
| /meter/total_energy_import | I64 kWh | Meter 0x0C83 |
| /meter/frequency | F32 Hz | Meter 0x0C07 |
| /dg/status | Enum | DG 0x0000 |
| /dg/output_power | I16 0.1kW | DG 0x000F |
| /dg/fuel_level | U16 0.1% | DG 0x0005 |
| /pv/status | Enum | PV 0x0000 |
| /pv/ac_power | I16 W | PV 0x000F |
| /pv/daily_energy | U32 Wh | PV 0x0013 |
| /pv/irradiance | U16 W/m² | PV 0x0017 |
| /gpio/di[0..7] | bool | GPIO |
| /gpio/do[0..7] | bool | GPIO |
| /control/ems_state | Enum | State Machine |
| /control/source_priority | array | Ctrl Mgr |

## 15.4 Control Modes & Algorithms

| Algorithm | Inputs | Output |
| --- | --- | --- |
| State Machine | All interlocks (Sec 3.3) | EMS state transitions |
| Source Priority | Grid/Solar/BESS/DG avail, Day/Night, irradiance | Active source selection |
| SOC Dispatch | SOC, L1/L2/L3/cutoff | Power with derating |
| Peak Shaving | Meter P, threshold | Discharge to cap import |
| Schedule Exec | Time, windows | Timed power |
| 96-Point Curve | 96-pt table | 15-min interpolated |
| Power Derating | Cell V/T, SOC | Reduced limit |
| Multi-Rack Balance | Per-rack SOC | Distribution |
| BTMS Management | Cell T, ambient T, coolant T | BTMS mode + setpoint |
| DG Auto-Start | Grid loss + SOC < threshold | DG start cmd + ATS |
| Reactive Q | Grid Q, PF target | kVAr setpoint |
| Emergency | Fire, E-Stop, IMD | PCS stop + contactors |

# 16. Certifications & Standards

| Standard | Scope | EMS Impact |
| --- | --- | --- |
| IEC 62619 | Battery safety | Alarm thresholds |
| IEC 62477 | PCS safety | Protection regs |
| UL 9540/9540A | ESS safety | Safety logging, FSS, thermal |
| UL 1741 | Inverter | Grid protection |
| IEC 61850 | Substation comm | Future MMS/GOOSE |
| IEEE 1547 | DER interconnect | V/f ride-through |
| IEC 62682 | Alarm management | 3-tier lifecycle |
| ISO 26262 | Functional safety | ASIL-B, dual-ch E-Stop |
| IEC 61508 | Industrial safety | SIL-2 functions |
| IS 16270 | BIS Li-ion (India) | BMS thresholds |
| CEA Regs | Grid storage (India) | Reactive, freq response |

# 17. Libraries & Dependencies

| Library | Module | Purpose |
| --- | --- | --- |
| python-can + cantools | comm_mgr | CAN + DBC |
| pymodbus | comm_mgr | Modbus TCP/RTU (PCS, BTMS, Meter, DG, PV) |
| paho-mqtt | cloud_mgr | MQTT TLS |
| fastapi + uvicorn | hmi_server | HTTP + WebSocket |
| pyarrow + duckdb | logger | Parquet + SQL |
| numpy | control/diag | Array ops |
| pyyaml + jsonschema | config_mgr | Config + validation |
| pyzmq | all | ZeroMQ IPC |
| cryptography | ota/cloud | TLS, X.509 |
| SocketCAN + libgpiod | comm_mgr (C) | CAN + GPIO |
| POSIX shm + pthreads | data/safety (C) | RTDB + RT threads |
| React.js + Chart.js + Tailwind | hmi frontend | SPA + charts |

# 18. Development Roadmap

| Phase | Weeks | Deliverables |
| --- | --- | --- |
| 1: Foundation | 8–10 | RTDB, Comm Mgr (CAN BMU→EMS + PCS + BTMS + Meter Modbus), Safety Mgr (E-Stop, Fire, all DO), Logger, Config. |
| 2: Control | 6–8 | State Machine (Sec 3), Interlock logic, Control Mgr (modes + source priority), Alarm Mgr (3-tier + indicators). |
| 3: HMI | 6–8 | 7 ReVx screens. Scheduler. DG + PV comm integration. |
| 4: Cloud | 4–6 | MQTT (Sec 8.3 schema), OTA. Firewall + network config. |
| 5: Advanced | 4–6 | Peak Shaving, Multi-rack, Reactive Q, DG auto-start, BTMS management, CAN FD. |
| 6: Certify | 4–6 | Scale test. ISO 26262 FMEA. UL 9540. Cybersecurity audit. |

# 19. Scaling Examples

| Metric | Small (215kWh) | Medium (1MWh) | Large (6MWh) |
| --- | --- | --- | --- |
| Clusters | 1 | 2 | 8 |
| Modules/Rack | 5 | 10 | 10 |
| Cells/Module | 16S | 54S | 54S |
| Total Cells | 320 | 8,640 | 34,560 |
| Data Points | ~700 | ~11,000 | ~43,000 |
| CAN | 2.0B | FD | FD+ETH |
| Modbus Devices | 4 (PCS+Meter+BTMS+DG) | 4–6 | 4–8 |
| MQTT Topics | ~15 | ~30 | ~80 |
| SSD/Day | ~25 MB | ~400 MB | ~1.5 GB |

# 20. Per-Deployment Requirements

| # | Item | Type | Impact |
| --- | --- | --- | --- |
| 1 | Cells/module (16S–108S) + modules/rack (3–20) | Config | system_config |
| 2 | Racks/cluster + cluster count | Config | system_config |
| 3 | BMS DBC files (vendor L1/L2) | Protocol | bms_config |
| 4 | PCS register map | Protocol | pcs_config |
| 5 | BTMS type (liquid/air) + vendor register map | Protocol | btms_config |
| 6 | Meter model (PM5xxx or other) + register map | Protocol | meter_config |
| 7 | DG type (smart/relay) + controller register map | Protocol | dg_config |
| 8 | PV inverter vendor + register map | Protocol | pv_config |
| 9 | I/O wiring (DI/DO per Section 5) | Hardware | gpio_config |
| 10 | IP addresses (LAN subnet, WAN) | Network | network_config |
| 11 | MQTT broker URL + site_id + auth certs | Cloud | cloud_config |
| 12 | Source priority overrides (Day/Night) | Control | control_config |
| 13 | Derating curves + SOC levels | Control | control_config |
| 14 | Grid code (country/utility) | Regulatory | control_config |
| 15 | Alarm thresholds per signal | Config | alarms_config |
| 16 | Safety cert target (ASIL/SIL) | Regulatory | Safety Mgr depth |

# 21. Data Logging & Historian Specification

## 21.1 Logging Architecture

The Logger module captures all RTDB signals at configurable rates and writes to Apache Parquet files on the NVMe SSD. DuckDB provides SQL query capability for trend charts, diagnostics, and data export. JSONL files capture discrete events (alarms, state changes, operator actions).

## 21.2 Log Channel Matrix

Each signal category has a defined logging rate, retention period, and storage estimate:

| Channel | Signals | Log Rate | Format | Retention | Storage/Day (Medium 1MWh) | Purpose |
| --- | --- | --- | --- | --- | --- | --- |
| BMS Cell Voltages | All cell_voltage[K] per rack | 1 Hz | Parquet (U16) | 90 days | ~140 MB | Cell health trending, balancing analysis |
| BMS Cell Temps | All cell_temp[N] per rack | 1 Hz | Parquet (I16) | 90 days | ~25 MB | Thermal trending, BTMS validation |
| BMS Pack Data | SOC, pack_V, pack_I, state per rack | 1 Hz | Parquet | 90 days | ~5 MB | SOC accuracy, capacity fade |
| BMS Extremes | V_min, V_max, T_min, T_max with IDs | 1 Hz | Parquet | 90 days | ~2 MB | Cell outlier detection |
| PCS AC Telemetry | 3-phase V, I, P, Q, PF, freq | 1 Hz | Parquet | 90 days | ~8 MB | Grid compliance, PCS efficiency |
| PCS DC Telemetry | Battery V, I, DC power, bus V | 1 Hz | Parquet | 90 days | ~3 MB | Round-trip efficiency |
| PCS Temps + State | IGBT, ambient, inductance, grid state | 1 Hz | Parquet | 90 days | ~2 MB | PCS health |
| PCS Fault Words | 0x1700–0x1707 | On change | JSONL | 1 year | <1 MB | Fault root cause |
| BTMS Telemetry | Coolant temps, flow, mode, fan/pump | 1 Hz | Parquet | 90 days | ~3 MB | Cooling performance |
| BTMS Alarms | Alarm words 0x0200–0x0202 | On change | JSONL | 1 year | <1 MB | BTMS fault history |
| Meter Data | 3-phase V, I, P, Q, PF, kWh | 1 Hz | Parquet | 90 days | ~8 MB | Revenue metering, grid compliance |
| Meter Energy | Import/export kWh accumulators | 5 min | Parquet | 5 years | ~50 MB/yr | Billing, warranty, performance |
| DG Telemetry | Status, V, I, P, RPM, fuel, temps | 1 Hz (running) | Parquet | 90 days | ~2 MB | DG efficiency, maintenance |
| DG Run Log | Start/stop events, run hours | On event | JSONL | 5 years | <5 MB/yr | Maintenance scheduling |
| PV Telemetry | DC/AC power, energy, irradiance | 1 Hz (daytime) | Parquet | 90 days | ~3 MB | PV performance ratio |
| GPIO States | DI[0..7], DO[0..7] | On change + 60s | JSONL | 1 year | <1 MB | Safety audit trail |
| EMS Control | State, mode, setpoint, source priority | 1 Hz | Parquet | 90 days | ~2 MB | Control decisions audit |
| Alarms | All alarm events (IEC 62682) | On event | JSONL | 5 years | ~10 MB/yr | Alarm rationalization, compliance |
| Operator Actions | Login, ACK, mode change, setpoint | On event | JSONL | 5 years | ~5 MB/yr | Audit trail |
| Comm Health | Per-device latency, error rate, uptime | 10 s | Parquet | 90 days | <1 MB | Diagnostics |

## 21.3 Storage Estimates

| Deployment | 1 Hz Parquet/Day | Events JSONL/Day | 90-Day Total | 5-Year Events | SSD Recommended |
| --- | --- | --- | --- | --- | --- |
| Small (215 kWh) | ~30 MB | ~1 MB | ~2.8 GB | ~300 MB | 128 GB |
| Medium (1 MWh) | ~200 MB | ~3 MB | ~18 GB | ~1 GB | 256 GB |
| Large (6 MWh) | ~800 MB | ~10 MB | ~73 GB | ~4 GB | 512 GB |

## 21.4 Data Export & Warranty Claims

The HMI provides CSV/Parquet export for any time range and signal set. For warranty claims, a standardized export includes: cell voltage trends (all cells, 1 Hz, incident window ±24 hours), temperature trends, SOC/SOH history, alarm log, PCS fault words. DuckDB query API enables cloud-side analytics dashboards and predictive maintenance.

## 21.5 Historian Query Interface

HMI trend charts use the DuckDB SQL API: SELECT timestamp, cell_voltage FROM bms_cell_v WHERE cluster=1 AND rack=2 AND module=3 AND cell=5 AND timestamp BETWEEN '2026-02-01' AND '2026-02-25' ORDER BY timestamp. Query latency target: <500ms for 90-day single-cell query, <2s for 90-day all-cells query.

# 22. Cybersecurity

## 22.1 Threat Model

The EMS is a critical infrastructure component. Threat categories: (1) Unauthorized remote access via WAN/LTE. (2) Local network intrusion via ETH0 LAN. (3) Physical access to USB/serial ports. (4) Supply chain attack via OTA firmware. (5) Insider threat via HMI credentials.

## 22.2 Network Security

| Control | Implementation | Notes |
| --- | --- | --- |
| Network segmentation | ETH0 (LAN) isolated from ETH1 (WAN). No IP forwarding between interfaces. | iptables FORWARD DROP |
| Firewall | Default-deny on WAN (ETH1). Only outbound 8883 (MQTT), 123 (NTP), 53 (DNS). | See Section 8.2 |
| No inbound WAN | Zero listening ports on ETH1. EMS initiates all cloud connections. | MQTT client, not server |
| LAN access control | MAC address whitelist for ETH0. Only known PCS, Meter, HMI IPs allowed. | iptables + arp-binding |
| SSH hardening | Key-based auth only (no passwords). Root login disabled. Port 22 on ETH0 only. | sshd_config |
| Modbus isolation | Modbus TCP (502) on LAN only. No authentication (protocol limitation). Physical isolation. | Compensated by network segmentation |

## 22.3 TLS & Certificate Management

| Component | Protocol | Certificate | Provisioning | Rotation |
| --- | --- | --- | --- | --- |
| MQTT to Cloud | TLS 1.3 | Mutual TLS (mTLS): EMS client cert + broker CA cert | Factory provisioned or OTA on first boot | Annual auto-renewal via ACME or cloud API |
| HMI WebSocket | WSS (TLS) | Self-signed CA cert installed on touchscreen browser | Generated at first boot. Operator accepts. | Regenerate on config reset |
| OTA Firmware | HTTPS | Anthropic/ReVx code-signing CA cert | Embedded in bootloader (immutable) | CA cert rotated via dual-key scheme |
| SSH | SSH | RSA 4096 or Ed25519 key pair | Engineer provisions key during commissioning | Key rotation per site policy |

## 22.4 Authentication & Authorization

| Role | Access Level | Auth Method | Session | Capabilities |
| --- | --- | --- | --- | --- |
| Guest | Read-only HMI | None (local display) | Persistent | View Dashboard, Cluster, Cell Details. No control. |
| Operator | Full HMI + control | Username + password (bcrypt hash) | 30 min timeout | Start/Stop, Mode change, ACK alarms, view Settings. |
| Engineer | Full + config + SSH | Username + password + optional TOTP | 60 min timeout | Edit config files, firmware update, calibration, SSH. |
| Cloud (Remote) | API commands only | mTLS client cert + API key | Per-request | Remote setpoint, schedule push, OTA trigger. No SSH. |

Password policy: minimum 12 characters, complexity required, max 5 failed attempts → 30 min lockout. Passwords stored as bcrypt hashes in /etc/ems/auth.db (not in YAML config). All auth events logged to JSONL audit trail.

## 22.5 OTA Firmware Security

| Step | Action | Verification |
| --- | --- | --- |
| 1. Download | Cloud pushes signed firmware bundle to EMS via MQTT command topic | TLS 1.3 transport encryption |
| 2. Signature verify | EMS verifies Ed25519 signature against embedded ReVx public key | Reject if signature invalid. Log attempt. |
| 3. Integrity check | SHA-256 hash of firmware image compared to manifest | Reject if mismatch |
| 4. Version check | Firmware version must be > current (no downgrade unless Engineer override) | Prevent rollback attacks |
| 5. Install to B partition | Write to inactive A/B partition. Do not touch running partition. | Atomic update |
| 6. Reboot + health check | Boot from B. Run self-test (comms, RTDB, GPIO). 5-minute watchdog. | If health check fails → auto-rollback to A |
| 7. Commit | Mark B as active after successful health check | A becomes fallback |

## 22.6 Audit Logging

All security-relevant events are logged to /var/log/ems/audit.jsonl with tamper-evident sequential numbering:

| Event Type | Fields Logged | Retention |
| --- | --- | --- |
| Login success/failure | Timestamp, username, role, IP, success/fail, lockout | 5 years |
| Session timeout | Timestamp, username, duration | 5 years |
| Config change | Timestamp, user, file, old_hash, new_hash | 5 years |
| OTA attempt | Timestamp, version, source, signature_valid, result | 5 years |
| SSH session | Timestamp, key_fingerprint, IP, commands (optional) | 5 years |
| Alarm ACK | Timestamp, alarm_id, user | 5 years (also in alarm log) |
| E-Stop / Fire | Timestamp, trigger, DI states, DO actions | 5 years |
| Cloud command | Timestamp, topic, action, source_cert | 5 years |

## 22.7 Physical Security

USB ports: Disabled in OS by default (usbguard). Engineer must enable for maintenance with auth.

Serial console: Disabled. Engineer boot with UART requires physical jumper inside enclosure.

Limit switch (DI-2): Logs door open events. Optional: block PCS start when door open (configurable).

SSD encryption: LUKS full-disk encryption for telemetry SSD. Key derived from TPM or hardware serial.

# 23. FMEA — Failure Mode & Effects Analysis (ISO 26262)

This FMEA covers the EMS controller and its interfaces. Ratings per ISO 26262: Severity (S1–S3), Occurrence (O1–O5), Detection (D1–D5). RPN = S × O × D. Target ASIL-B for safety-critical functions.

## 23.1 Severity Scale

| Rating | Level | Description | Example |
| --- | --- | --- | --- |
| S1 | Minor | No safety impact. Operational inconvenience. | HMI display freeze, cloud disconnect |
| S2 | Moderate | Potential equipment damage. No human injury. | PCS overcharge, cell OV without thermal event |
| S3 | Severe | Potential thermal runaway, fire, or human injury. | Uncontrolled discharge, contactor weld, fire |

## 23.2 Occurrence Scale

| Rating | Level | Description | Rate |
| --- | --- | --- | --- |
| O1 | Very Low | Extremely unlikely in product lifetime | <1 per 10⁶ hours |
| O2 | Low | Unlikely but possible | 1 per 10⁵ hours |
| O3 | Moderate | Occasional | 1 per 10⁴ hours |
| O4 | High | Likely to occur | 1 per 10³ hours |
| O5 | Very High | Frequent or systematic | 1 per 10² hours |

## 23.3 Detection Scale

| Rating | Level | Description | Example |
| --- | --- | --- | --- |
| D1 | Almost Certain | Hardware-independent detection within 100ms | Dual-channel E-Stop, HVIL loop |
| D2 | High | Automated detection within 1s | Heartbeat timeout, PCS fault word read |
| D3 | Moderate | Detected within 10s by monitoring | SOC drift, comm error counter |
| D4 | Low | Detected by periodic diagnostics | SOH degradation, sensor drift |
| D5 | Very Low | Undetected until manual inspection | Internal corrosion, latent firmware bug |

## 23.4 FMEA Table

| ID | Subsystem | Failure Mode | Effect | S | O | D | RPN | Detection Method | Mitigation / Control | ASIL |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| F-01 | CAN Bus | CAN bus failure (open/short) | Loss of BMS data. EMS blind to cell V/T/SOC. | S3 | O2 | D2 | 12 | Heartbeat timeout (1s). CAN error frame counter. | Immediate PCS shutdown (Safety Mgr). Redundant HVIL loop independent of CAN. | B |
| F-02 | CAN Bus | CAN message corruption (bit error) | Incorrect cell V or SOC read. Possible overcharge/overdischarge. | S3 | O3 | D2 | 18 | CAN CRC check (protocol-level). Plausibility check on V/T deltas. | Reject corrupted frames. Trigger alarm if error rate exceeds threshold. | B |
| F-03 | BMS | BMU heartbeat loss | EMS cannot confirm BMS is alive. | S3 | O2 | D1 | 6 | 300ms heartbeat monitor. <1s detection. | PCS stop within 1s. Safety Mgr GPIO-level. Independent HVIL. | B |
| F-04 | BMS | SOC calculation error in BMU | Incorrect SOC causes overcharge (>100%) or overdischarge (<0%). | S3 | O2 | D3 | 18 | EMS cross-checks SOC vs cell V_min/V_max. Coulomb counting shadow. | Cell V limits (IL-5, IL-6) are primary protection, not SOC. | B |
| F-05 | BMS | Cell V sensor failure (wire open) | Missing or stuck cell voltage. May miss OV/UV condition. | S3 | O3 | D2 | 18 | Wire-open diagnostics (L1 DBC). Delta_V anomaly detection. | BMU flags wire-open in DTC. EMS blocks PCS start. | B |
| F-06 | BMS | Contactor weld (stuck closed) | Rack cannot be isolated. Energy flows uncontrolled. | S3 | O1 | D2 | 6 | Contactor feedback mismatch (cmd vs status). Switched vs unswitched V comparison. | Fuse backup. E-Stop hardwired chain. HVIL loop. Annual contactor inspection. | B |
| F-07 | PCS | Modbus comm loss to PCS | EMS cannot send setpoints or read status. | S2 | O3 | D2 | 12 | Modbus timeout (0x1648). Response timeout counter. | PCS self-protects on comm loss (built-in). EMS transitions to FAULT state. | A |
| F-08 | PCS | PCS ignores power setpoint | PCS runs at wrong power. Over/undercharge. | S2 | O2 | D2 | 8 | Compare setpoint (0x500E) with actual power (0x6039). Delta alarm. | If delta > 10% for >10s, force PCS off (0x0291=0). Safety Mgr backup. | A |
| F-09 | PCS | PCS internal fault (IGBT failure) | Uncontrolled power flow or PCS shutdown. | S2 | O2 | D1 | 4 | PCS fault words (0x1700–1707). PCS self-trips on hardware fault. | PCS has independent protection. EMS reads fault, transitions to FAULT, logs. | A |
| F-10 | Safety Mgr | Safety Manager crash/hang | E-Stop and fire responses delayed or lost. | S3 | O1 | D1 | 3 | HW watchdog (ECU-1170). If Safety Mgr doesn't pet watchdog in 2s → system reset. | Independent C process. PREEMPT_RT. Minimal dependencies. HW watchdog auto-recovery. | B |
| F-11 | Safety Mgr | GPIO driver failure | Cannot read E-Stop or drive PCS Em Stop output. | S3 | O1 | D1 | 3 | libgpiod error return codes. Periodic GPIO self-test (toggle spare DO, read back). | Hardwired E-Stop relay chain independent of GPIO. Dual-channel DI-6+DI-7. | B |
| F-12 | RTDB | RTDB shared memory corruption | All modules read garbage data. Cascading failures. | S3 | O1 | D2 | 6 | CRC-32 checksum on RTDB segments. Version counter. Writer validates before commit. | If CRC mismatch detected, freeze outputs (hold last good), alarm, restart data_manager. | B |
| F-13 | RTDB | RTDB update stall (writer hangs) | Stale data in RTDB. EMS acts on old values. | S2 | O2 | D2 | 8 | Timestamp per RTDB segment. Staleness detector (>2s = stale). | If stale, Safety Mgr ramps PCS to 0, transitions to FAULT. | A |
| F-14 | Control Mgr | Control Manager crash | No new setpoints issued. PCS holds last command. | S2 | O2 | D2 | 8 | systemd health check (10s). Process watchdog. | PCS has independent timeout (0x1648). systemd auto-restart within 5s. | A |
| F-15 | Control Mgr | Incorrect algorithm output (SW bug) | Wrong power setpoint. Potential overcharge/overdischarge. | S3 | O2 | D3 | 18 | Setpoint bounds checking (clamp to rated power). SOC/V cross-validation. | Control Mgr clamps output to min(PCS max, BMS current limit, config limit). Safety Mgr independent. | B |
| F-16 | HMI Server | HMI crash or WebSocket disconnect | Operator loses visibility. Cannot control via HMI. | S1 | O3 | D2 | 6 | systemd auto-restart. WebSocket reconnect in React app. | System continues on last mode. Cloud provides backup visibility. Auto-restart <5s. | QM |
| F-17 | Cloud Mgr | MQTT connection lost | No remote monitoring or cloud commands. | S1 | O4 | D2 | 8 | MQTT keepalive (30s). Connection state in RTDB. | Local-first design. All control works without cloud. SSD buffers telemetry. Auto-reconnect. | QM |
| F-18 | Logger | SSD failure or full | Telemetry logging stops. No historical data. | S1 | O2 | D2 | 4 | Disk space monitor (alarm at 90%). SMART health check. | Alarm on disk low. Auto-purge oldest data. System operates without logging. | QM |
| F-19 | BTMS | BTMS comm loss | EMS cannot read/control thermal system. | S2 | O3 | D2 | 12 | Modbus timeout counter. BTMS alarm word check. | Conservative: derate PCS power. If cell T rising without BTMS, shutdown. | A |
| F-20 | BTMS | Cooling failure (pump/fan/compressor) | Cell temperature rises uncontrolled. Thermal runaway risk. | S3 | O2 | D2 | 12 | BTMS alarm word (pump fault, compressor fault). Cell T_max rising. | Derate to 50% at T_warning, stop PCS at T_alarm. Fire system (DI-3+4) as final backup. | B |
| F-21 | Meter | Meter comm loss | No revenue-grade measurement. Peak shaving blind. | S1 | O3 | D2 | 6 | Modbus timeout. Use PCS self-measurement as fallback. | Alarm. Fallback to PCS AC readings. Flag data as 'estimated' for billing. | QM |
| F-22 | DG | DG fails to start on command | No backup power during grid outage. BESS drains to cutoff. | S2 | O3 | D3 | 18 | DG status feedback (run status). Crank fail alarm. | Retry start 3x. Alarm if fail. Adjust BESS SOC strategy (preserve reserve). | A |
| F-23 | DG | DG overspeed / electrical fault | Unstable power to loads. Equipment damage. | S2 | O2 | D1 | 4 | DG internal protection + alarm words. EMS reads fault. | DG self-protects. EMS reads alarm, opens DG breaker, switches to BESS/Grid. | A |
| F-24 | PV | PV comm loss | Cannot read solar production. Day/Night detection affected. | S1 | O3 | D2 | 6 | Modbus timeout. Irradiance from fallback (time-based day/night). | Alarm. Fallback to time-based day/night. Solar power estimated from meter export. | QM |
| F-25 | E-Stop | E-Stop button mechanical failure (stuck) | Cannot trigger emergency shutdown manually. | S3 | O1 | D4 | 12 | Periodic E-Stop test (monthly, logged). Dual-channel DI-6+DI-7 cross-check. | Fire system (DI-3+4) as independent emergency path. Remote E-Stop via cloud command. | B |
| F-26 | Fire | Smoke sensor false alarm (single) | Nuisance alarm. No extinguisher activation. | S1 | O3 | D1 | 3 | Dual-confirmation required (Smoke AND Heat). Single sensor = warning only. | DO-1 (extinguisher) only activates on dual confirm. Warning alarm on single. | QM |
| F-27 | Fire | Smoke+Heat sensor both fail to detect fire | Fire undetected by EMS. Thermal runaway. | S3 | O1 | D4 | 12 | Cell T_max rate-of-rise (dT/dt) as independent detection via BMS. | BMS has independent thermal protection (HVIL). Container fire-rated walls. External FSS. | B |
| F-28 | Power | EMS power supply failure | EMS offline. No control. | S2 | O2 | D1 | 4 | PCS has independent timeout shutdown. BMS has HVIL. UPS recommended. | UPS for EMS (5–15 min). PCS/BMS self-protect. Graceful shutdown on UPS low. | A |
| F-29 | Config | Config file corruption/deletion | EMS cannot start or runs with wrong parameters. | S2 | O1 | D2 | 4 | JSON Schema validation on load. SHA-256 checksum. Backup copy. | Refuse to start on invalid config. Fall back to last-known-good backup. Alert. | A |
| F-30 | Firmware | OTA installs malicious/buggy firmware | System compromised or malfunctioning. | S3 | O1 | D1 | 3 | Ed25519 signature verification. Version check. Health watchdog post-update. | Signature must match ReVx key. Auto-rollback if health check fails in 5 min. | B |

## 23.5 Risk Priority Summary

| RPN Range | Risk Level | Count | Action Required |
| --- | --- | --- | --- |
| 1–6 | Low | 12 | Accept. Monitor via diagnostics. |
| 7–12 | Medium | 10 | Mitigate via software controls. Verify in testing. |
| 13–18 | High | 8 | Requires dedicated mitigation. Verify in ASIL testing. Review annually. |
| >18 | Critical | 0 | Must reduce before deployment. Redesign if necessary. |

No failure modes exceed RPN 18. The highest-risk items (F-02, F-04, F-05, F-15, F-22 at RPN 18) all have multiple independent detection and mitigation layers. The architecture’s defense-in-depth (BMS HVIL independent of EMS, PCS self-protection independent of Modbus, hardwired E-Stop independent of GPIO driver, dual-channel fire detection) ensures no single failure can lead to an unmitigated S3 event.

# 24. Commissioning & Site Acceptance Test (SAT) Procedure

This procedure is executed by a ReVx Engineer during first deployment or after major hardware changes. All results recorded in the SAT Report. Estimated duration: 2–3 days for a medium (1 MWh) system.

## 24.1 Pre-Commissioning Checklist

| # | Item | Verification | Pass Criteria |
| --- | --- | --- | --- |
| PC-1 | Visual inspection | Inspect all cable connections, DIN rail mount, SSD installed, antenna (if LTE) | No loose connections, damage, or missing components |
| PC-2 | Power supply | Measure DC input voltage at ECU-1170 terminal | 9–36V DC within range |
| PC-3 | Network cables | Verify ETH0/ETH1 link LEDs. Ping test. | Link UP, ping < 1ms LAN |
| PC-4 | CAN bus wiring | Check CAN H/L, termination resistors (120Ω each end) | Resistance 60Ω between H-L |
| PC-5 | RS485 wiring | Check A/B polarity, termination, shield grounding | Continuity OK, no shorts |
| PC-6 | DI wiring | Toggle each DI source, verify correct pin mapping | Each DI reads correct state |
| PC-7 | DO wiring | Command each DO, verify field device activates | Each DO drives correct output |
| PC-8 | Configuration loaded | Verify all 14 YAML files present and validated | Config Manager reports OK |
| PC-9 | Time sync | Check NTP synchronization | Time within 100ms of reference |
| PC-10 | SSD mounted | Verify SSD detected and mounted at /mnt/data | df shows expected capacity |

## 24.2 Communication Verification

| # | Test | Procedure | Pass Criteria | Duration |
| --- | --- | --- | --- | --- |
| CV-1 | BMS CAN heartbeat | Power on BMS. Monitor candump on CAN0/CAN1. Verify SOC_Message frames arriving. | SOC_Message (0x98FF0003) received every 300ms per cluster. | 5 min |
| CV-2 | BMS DBC decode | Verify cantools decodes all L2 messages. Check SOC, pack V, pack I values vs BMS display. | Decoded values match BMS display ±0.5%. | 10 min |
| CV-3 | BMS cell data | Verify Cell_Voltages and Cell_Temps messages. Compare sample cells vs BMS local display. | All configured cells reporting. Values match ±1mV, ±0.5°C. | 15 min |
| CV-4 | PCS Modbus | Read 0x6020–0x605C. Verify voltages, state. Read 0x6000–0x6005 (version). | All registers readable. Version string matches PCS nameplate. | 5 min |
| CV-5 | PCS control test | Write 0x0291=1 (ON), wait 10s, verify 0x6057 state change. Write 0x0291=0. | PCS transitions to Standby/Run. Clean shutdown. | 5 min |
| CV-6 | Meter Modbus | Read PM5xxx registers. Compare voltage/frequency vs handheld meter. | Values match ±0.5V, ±0.01Hz. | 5 min |
| CV-7 | BTMS Modbus | Read all BTMS telemetry. Verify temperatures vs independent sensor. | Temps match ±1°C. Mode reads correctly. | 5 min |
| CV-8 | DG Modbus (smart) | Read DG status. Send start command. Verify engine starts. | DG responds to start/stop. Telemetry matches. | 10 min |
| CV-9 | PV Modbus | Read PV inverter telemetry. Verify power matches PV display. | Power matches ±2%. | 5 min |
| CV-10 | Cloud MQTT | Verify MQTT connects (TLS). Publish test telemetry. Receive test command. | Messages appear on cloud dashboard. Round-trip < 5s. | 10 min |

## 24.3 I/O Verification

| # | Test | Procedure | Pass Criteria |
| --- | --- | --- | --- |
| IO-1 | DI-0 ACDB | Open/close ACDB breaker. Verify DI-0 state changes in HMI. | State matches within 100ms |
| IO-2 | DI-1 Flood | Simulate flood sensor (short input). Verify alarm generated. | Alarm fires. Clears on remove. |
| IO-3 | DI-2 Limit Switch | Open container door. Verify log entry. | Event logged with timestamp |
| IO-4 | DI-3 Smoke | Simulate smoke input. Verify warning (single sensor). | Warning alarm. No extinguisher (single). |
| IO-5 | DI-4 Heat | Simulate heat input. Verify warning. | Warning alarm. |
| IO-6 | DI-3+4 Fire | Simulate both Smoke+Heat. Verify full fire sequence. | DO-1 activates. DO-5+DO-0+DO-6+DO-4 activate. State → FIRE. |
| IO-7 | DI-5 Ext. Status | Activate fire ext. Verify DI-5 feedback reads discharged. | Status reads correctly. |
| IO-8 | DI-6+7 E-Stop | Press E-Stop button. Verify full emergency sequence. | DO-5+DO-0+DO-6+DO-4 activate. State → E-STOP. PCS stops. |
| IO-9 | DO-2 Warning | Trigger warning alarm. Verify yellow lamp ON. | Lamp activates. |
| IO-10 | DO-3 Running | Start PCS. Verify green lamp ON. Stop → OFF. | Lamp tracks PCS state. |

## 24.4 Interlock Verification

| # | Test | Procedure | Pass Criteria |
| --- | --- | --- | --- |
| IL-T1 | SOC cutoff block | Set SOC below cutoff. Attempt discharge start. | Start blocked. Alarm displayed. |
| IL-T2 | Cell OV block | Inject V_max above threshold (via BMS test mode). Attempt charge. | Start blocked. |
| IL-T3 | E-Stop latch | Press E-Stop. Attempt start without physical reset. | Start blocked until reset + ACK. |
| IL-T4 | PCS fault block | Induce PCS fault (disconnect phase). Attempt restart. | Blocked until fault reset (0x5064). |
| IL-T5 | BMS heartbeat | Disconnect CAN. Attempt start. | Blocked. Heartbeat alarm. |
| IL-T6 | IMD insulation | Reduce IMD R_iso below threshold (if testable). | Start blocked. |

## 24.5 Functional Test (First Charge/Discharge)

| # | Test | Procedure | Pass Criteria | Duration |
| --- | --- | --- | --- | --- |
| FT-1 | First charge (10% power) | Schedule mode: 10% rated power charge for 15 min. | SOC increases. Cell V stable. No alarms. BTMS responds. | 20 min |
| FT-2 | First discharge (10%) | Schedule: 10% discharge for 15 min. | SOC decreases. Grid meter shows export. | 20 min |
| FT-3 | Full power charge | Ramp to 100% rated charge power. Hold 5 min. | PCS tracks setpoint ±2%. Temps stable. No derating. | 10 min |
| FT-4 | Full power discharge | Ramp to 100% rated discharge. Hold 5 min. | Setpoint tracking. Meter matches PCS. | 10 min |
| FT-5 | Derating test | Discharge until SOC hits L1. Verify power derates. | Power reduces per derating curve in control_config. | Variable |
| FT-6 | Source priority | Disconnect grid (open ACDB). Verify BESS/DG takes over. | Source switches per Section 4 truth table. | 10 min |
| FT-7 | Graceful shutdown | Operator Stop via HMI. Verify sequence. | Power ramps to 0, PCS off, contactors open, state → STANDBY. | 5 min |

## 24.6 SAT Report Sign-Off

All tests documented with: Test ID, Date/Time, Tester name, Result (PASS/FAIL/N-A), Notes, Evidence (screenshot/photo). Both ReVx Engineer and Customer representative sign the SAT Report. Any FAIL items documented with remediation plan and re-test date.